# Advanced Prognostics and Remaining Useful Life (RUL) Forecasting for Vapor-Compression HVAC/R Systems

The evolution of heating, ventilation, air conditioning, and refrigeration (HVAC/R) maintenance strategies has steadily progressed from reactive troubleshooting to proactive, data-driven condition monitoring. Within this domain, the Li & Braun residual method has established itself as a highly effective approach for Fault Detection and Diagnostics (FDD) in vapor-compression cycles. By continuously computing the differential—or residual—between observed thermodynamic states and the expected states generated by a healthy baseline model operating under identical boundary conditions (e.g., source temperature, sink temperature, and compressor speed), the method effectively decouples equipment health from transient environmental loads1.

However, point-in-time diagnostic classification pipelines, while adept at identifying the presence and immediate severity of a fault, lack temporal foresight. To achieve true predictive maintenance, the analytical framework must transition from static classification to dynamic time-series forecasting. This necessitates extrapolating degrading residuals over time, anticipating the trajectory of soft faults (such as progressive coil fouling or slow refrigerant leakage), and estimating the Remaining Useful Life (RUL) before a critical operational threshold is breached, aligning with the failure prognostics standards defined in ISO 13381-13.

This report provides an exhaustive architectural and methodological blueprint for expanding steady-state FDD pipelines into continuous RUL forecasting engines. It systematically evaluates open-access thermodynamic datasets, state-of-the-art synthetic degradation modeling tools, advanced temporal forecasting algorithms, and the practical challenges of deploying these systems in the presence of real-world equipment dynamics, such as variable-speed compressor cycling and oil return sequences.

## 1. Target Time-Series Datasets for HVAC/R Prognostics

A fundamental bottleneck in the development of prognostic algorithms for vapor-compression systems is the severe scarcity of open-source, high-quality, run-to-failure (RTF) data. Natural degradation occurs over months or years, making continuous, high-fidelity data collection cost-prohibitive. Consequently, most academic and industrial datasets are designed for classification, wherein faults are artificially injected as discrete step-changes in severity.

Despite this limitation, several highly documented datasets provide the essential internal thermodynamic cycle variables (e.g., suction/discharge pressures, refrigerant temperatures, superheat, subcooling) necessary for computing Li & Braun residuals. While these datasets may require synthetic temporal interpolation to simulate continuous degradation, they serve as the foundational ground truth for establishing healthy baseline models and mapping the multi-dimensional residual space at specific degradation milestones.

### 1.1 ASHRAE RP-1043: Centrifugal Chiller Fault Dataset

The ASHRAE RP-1043 dataset remains the preeminent benchmark for chiller fault detection and diagnosis6. Derived from experimental data on a 90-ton centrifugal chiller, the dataset captures normal operation alongside seven distinct faulty conditions, each introduced at four discrete severity levels7. The faults include condenser fouling (modeled by blocking 12%, 20%, 30%, and 45% of tubes), refrigerant leakage (reducing charge by 10% to 40%), refrigerant overcharge, non-condensable gas accumulation, reduced evaporator and condenser water flows, and excessive oil7.

Because the faults in RP-1043 are imposed as static step-changes rather than continuous temporal degradation, the dataset cannot be utilized directly for training temporal RUL models without synthetic manipulation6. However, the inclusion of 64 exact steady-state thermodynamic variables makes it indispensable for defining the residual thresholds that precede critical failure7.

| Feature Category | Typical Sensor Column Names | Description |
| --- | --- | --- |
| Temperatures | TEO, TEI, TCO, TCI, TRC, TRE | Evaporator/Condenser water out/in, Saturated refrigerant temp in condenser/evaporator8. |
| Pressures | Cond_P, Evap_P, PO_feed | Condenser pressure, Evaporator pressure, Oil feed pressure8. |
| Flow Rates | FWC, FWE, Ref_MassFlow | Water flow rate in condenser/evaporator, Refrigerant mass flow rate8. |
| Power Dynamics | W_comp, Comp_Speed | Compressor electrical power consumption, Compressor RPM. |

### 1.2 LBNL/DOE FDD Datasets (Figshare)

The Lawrence Berkeley National Laboratory (LBNL), in partnership with the Department of Energy (DOE), curates a massive repository of FDD datasets stored on Figshare, accessible via the persistent identifier DOI: 10.6084/m9.figshare.c.64863499. This collection encompasses operational data from Rooftop Units (RTUs), Air Handling Units (AHUs), Fan Coil Units (FCUs), Boiler Plants, and Chiller Plants9.

These datasets provide 1-minute interval time-series data capturing faults such as air-side and water-side coil fouling, stuck dampers, sensor biases, and valve leakages13. For example, the FCU dataset contains granular files like FCU_FilterRestriction_10%.csv and FCU_VLVLeak_Cooling_20.csv12. While the data perfectly captures natural diurnal load variations and continuous operational cycles, the fault progression remains static, requiring similar synthetic extrapolation for RUL applications12.

| Feature Category | Typical Sensor Column Names | Description |
| --- | --- | --- |
| Air-Side Thermodynamics | RTU: supply air temperature, RTU: return air relative humidity | Supply and return air thermal states13. |
| Airflow & Pressure | RTU: supply air volumetric flow rate, RTU: static pressure | Volumetric flow () and duct static pressure (Pa)13. |
| Component Electrical | RTU: compressor 1 electricity, RTU: condenser fan 1 electricity | Discrete component-level power consumption (Wh)13. |

### 1.3 ASHRAE RP-1312 and NIST Heat Pump Datasets

The ASHRAE RP-1312 dataset, accessible via DOI: 10.25984/1824861 through the Open Energy Data Initiative, provides simulated time-series data for AHUs and RTUs under various fault conditions, generated using EnergyPlus models15. For residential and light-commercial heat pumps, the National Institute of Standards and Technology (NIST) has published critical FDD reports (e.g., NIST TN 1848, NIST TN 1648, NIST TN 1774)18. These datasets detail the thermodynamic cycle responses to duct leakage, refrigerant undercharge, and low indoor airflow18. Crucially for the Li & Braun methodology, the NIST datasets capture highly specific cycle variables such as superheat, subcooling, and two-phase enthalpy splits21.

Additionally, the HEAPO (Heat Pump Optimization) dataset hosted on Zenodo provides open-access time-series data for heat pumps. However, it leans heavily toward smart meter building-level electricity consumption and weather data, lacking the deep internal cycle variables required for pure thermodynamic residual modeling24. Similar Zenodo repositories (e.g., DOI: 10.5281/zenodo.18138668) provide synthetic multivariate refrigerator time-series data, which can serve as a proxy for evaluating time-series architectures before deployment on heavy commercial HVAC systems25.

## 2. Run-to-Failure Synthetic Generation Benchmarks

Because naturally occurring, multi-month run-to-failure data for vapor-compression cycles is exceptionally rare in the public domain, prognostic model development relies heavily on the generation of synthetic benchmarks. The state-of-the-art methodology involves coupling high-fidelity physical simulations with stochastic degradation kinetics to produce realistic, dynamic time-series data.

### 2.1 Physics-Based Degradation via Modelica and BOPTEST

While tools like EnergyPlus are highly effective for building-level energy modeling, they utilize simplified empirical performance curves that lack the granular internal physics required to calculate specific thermodynamic residuals like evaporator superheat or compressor discharge temperature. Instead, the industry standard for component-level thermodynamic simulation is the equation-based, object-oriented modeling language Modelica26.

The open-source Modelica Buildings Library (hosted at github.com/lbl-srg/modelica-buildings) provides foundational components such as Buildings.Fluid.Chillers.ElectricEIR and fundamental heat exchanger models via Buildings.Fluid.HeatExchangers26. To orchestrate the dynamic injection of faults during runtime, researchers utilize the BOPTEST (Building Optimization Performance Test) framework, hosted by IBPSA (github.com/ibpsa/project1-boptest)30. BOPTEST exposes a Python API that allows external scripts to interact with the Modelica simulation at every time step, enabling the continuous alteration of physical parameters to simulate degradation.

### 2.2 Injecting Stochastic Physical Degradation Kinetics

To generate a run-to-failure dataset, physical fault models must be coupled with stochastic kinetic equations. Rather than imposing a discrete 20% blockage on a condenser, the BOPTEST Python wrapper continuously modifies the internal parameters of the Modelica components over a simulated multi-month horizon.

Condenser and Evaporator Coil Fouling: Fouling is mathematically modeled as a gradual increase in thermal resistance, which subsequently decreases the overall heat transfer coefficient () of the coil. In a Modelica heat exchanger model, the nominal  (overall heat transfer coefficient multiplied by area) value can be dynamically degraded using an asymptotic or exponential function:

Where  represents the asymptotic maximum fouling resistance,  is the deposition rate constant determined by local air or water quality, and  is a stochastic noise term (e.g., a Wiener process) simulating the randomness of particulate accumulation. As  increases, the condenser approach temperature naturally drifts upward. To meet the cooling load, the simulated compressor is forced to draw more power, generating continuous, interdependent residual drift trajectories across multiple sensors—precisely the data structure required to train prognostic algorithms.

Slow Refrigerant Leakage: Refrigerant leakage can be simulated by continuously extracting mass from the closed thermodynamic loop. This is achieved in Modelica by manipulating a mass flow sink connected to the liquid line. The leak rate  can be modeled as a function of the internal system pressure  and the degradation of a mechanical seal over time:

Where the orifice area  expands slowly over time following a linear drift or a Paris-Erdogan crack propagation model32. As the refrigerant charge diminishes, the Modelica solver dynamically recalculates the diminishing subcooling and increasing superheat. If simulating modern low-GWP zeotropic refrigerant blends (e.g., R-454B), the simulation must also account for blend fractionation, where the leak alters the composition of the remaining refrigerant, further compounding the drift in the superheat residual35.

## 3. State-of-the-Art Time-Series Architectures for FDD Residuals

Once the raw thermodynamic variables are processed through the Li & Braun method to yield steady-state residuals (), the analytical objective shifts to temporal extrapolation. The prognostic model must predict when a degrading residual will cross a critical failure threshold. The selection of the extrapolation algorithm depends on the non-linearity of the degradation, the dimensionality of the residuals, and the available computational resources.

### 3.1 Classical Time-Series Forecasting: ARIMA and Prophet

Classical statistical methods such as Autoregressive Integrated Moving Average (ARIMA) and Facebook's Prophet have long been the baseline for time-series forecasting. ARIMA relies on differencing to make data stationary and uses linear combinations of past values and errors to predict the future. Prophet utilizes a decomposable time-series model with three main components: trend, seasonality, and holidays, framing the forecasting problem as a curve-fitting exercise38.

While computationally inexpensive, these classical methods consistently fail when applied to HVAC/R degradation residuals. ARIMA struggles fundamentally with non-linear degradation paths (such as the exponential drift of coil fouling) and cannot effectively handle multivariate interdependencies (e.g., the linked degradation of compressor power and discharge temperature). Prophet, while better at handling missing data and seasonal shifts, is fundamentally designed for business time-series and lacks the capacity to model complex thermodynamic state transitions38. Neither algorithm can process the high-dimensional, highly correlated sensor telemetry characteristic of modern vapor-compression cycles without significant feature engineering.

### 3.2 Bayesian Filtering: Kalman Filters and Particle Filters

For systems where the physics of failure is thoroughly understood and can be described mathematically, model-based Bayesian filtering techniques remain highly effective.

Extended Kalman Filters (EKF): The EKF linearizes nonlinear system dynamics using Taylor series expansions. Because it relies heavily on matrix operations rather than deep neural network weights, EKF is extremely computationally efficient, making it a popular choice for deployment directly on embedded microcontrollers within HVAC control boards39. However, EKF operates under the strict assumption that both the system dynamics and the measurement noise follow Gaussian distributions39. In real-world HVAC systems, degradation rates (such as stochastic bio-fouling or unpredictable refrigerant leaks) are often highly non-linear and non-Gaussian, leading the EKF to diverge or produce highly inaccurate RUL estimates over long horizons39.

Particle Filters (PF): Particle Filters address the limitations of EKF by utilizing Monte Carlo sampling, making them exceptional at handling non-linear and non-Gaussian degradation42. The PF algorithm maintains a set of "particles," where each particle represents a discrete hypothesis of the system's true degradation state.

- Prediction Phase: Each particle is propagated forward in time using a physical degradation state-transition model (e.g., a Paris-Erdogan drift equation)32.

- Update Phase: When a new HVAC residual is observed, the likelihood of each particle is evaluated based on how closely its predicted state matches the observed residual.

- Resampling Phase: Particles with high likelihoods are duplicated, while those with low likelihoods are discarded44.

The paramount advantage of Particle Filters in predictive maintenance is their ability to output a Probability Density Function (PDF) of the Remaining Useful Life, providing maintenance teams with actionable confidence intervals (e.g., a 90% probability of critical failure within 14 to 18 days)42. However, PFs demand immense computational power to process thousands of particles at every time step, rendering them unsuitable for low-power edge devices and IoT sensor nodes41.

### 3.3 Deep Learning: LSTMs and Temporal Convolutional Networks (TCNs)

When physical degradation models are unknown or too complex to derive analytically, data-driven architectures become the default. Recurrent Neural Networks (RNNs), specifically Long Short-Term Memory (LSTM) networks, and Temporal Convolutional Networks (TCNs) have historically dominated this space47.

LSTMs maintain a hidden state that captures sequential dependencies, theoretically allowing them to track the slow drift of a condenser fouling residual. However, LSTMs process data sequentially, which severely limits their ability to capture very long-term dependencies due to the vanishing gradient problem. A slow refrigerant leak may take six months to trigger a critical fault; an LSTM struggles to correlate the subtle drifts from month one with the catastrophic failure in month six. TCNs resolve some of this sequential bottleneck through dilated causal convolutions, allowing for exponentially larger receptive fields and parallel processing. Yet, both LSTMs and TCNs struggle with the highly erratic, multivariate relationships found in noisy HVAC telemetry.

### 3.4 The State-of-the-Art: Patch Time Series Transformer (PatchTST)

The current vanguard in multivariate time-series forecasting for predictive maintenance is the Transformer architecture, specifically the Patch Time Series Transformer (PatchTST)48. While standard Transformers (like those used in Natural Language Processing) treat each individual time step as a distinct token, this approach destroys local temporal semantic information and scales quadratically in attention computation, severely restricting the look-back window50.

PatchTST overcomes these limitations through two profound architectural innovations:

- Patching: The continuous residual time-series is divided into sub-sequence patches (e.g., windows of 16 time steps). Each patch is embedded as a single token45. This preserves the local temporal semantics (the immediate physical relationship between a measurement at time  and ) and drastically reduces the computational overhead50. By quadratically reducing the memory footprint of the attention maps, PatchTST can look back over vastly longer historical horizons (e.g.,  steady-state steps) to capture long-term macro-degradation trends50.

- Channel Independence: In standard multivariate forecasting, data from all sensors at a single time step are projected into a single token. PatchTST treats each time-series variable (each distinct residual) as an independent channel, applying the same Transformer backbone to each channel separately before fusing the outputs at the regression head45. This is critical for vapor-compression FDD: the degradation of a superheat residual behaves fundamentally differently than a subcooling or compressor power residual. Channel independence prevents the attention mechanism from conflating these distinct physical dynamics, allowing the model to track the individual trajectory of each thermodynamic variable45.

Implementation of PatchTST is readily accessible through open-source Python libraries such as neuralforecast (maintained by Nixtla) or pyFAST, which provide optimized, GPU-accelerated environments for training and deploying forecasting models49.

## 4. Handling Real-World Dynamics: Regime Changes, Variable Speeds, and Cycling

The transition from quasi-steady-state experimental data to real-world deployment introduces severe operational challenges. Real HVAC/R systems do not operate in continuous, unvarying states; they undergo frequent on/off cycling, load modulation, and environmental regime shifts. If raw, unfiltered telemetry is fed directly into a residual generator and subsequently into a prognostic model, transient spikes will be falsely identified as severe degradation, triggering false positive RUL alerts that erode trust in the predictive maintenance system56.

### 4.1 Variable Frequency Drives (VFDs) and Oil Return Dynamics

Modern heat pumps and chillers extensively utilize VFDs to modulate compressor speed, dramatically enhancing part-load efficiency58. However, VFDs introduce complex operational artifacts. When a scroll or reciprocating compressor operates at significantly reduced speeds (e.g., below 40-50 Hz), the refrigerant mass flow velocity drops58. If the suction line velocity falls below approximately 0.8 m/s, the refrigerant loses the kinetic energy required to effectively entrain lubricating oil61. Consequently, the oil separates and pools in the evaporator and suction lines, leading to oil starvation at the compressor crankcase61.

To prevent catastrophic mechanical failure, VFD-driven systems execute periodic "flush cycles" or "oil management overrides"63. During these cycles, the compressor speed is forcibly boosted to maximum capacity for several minutes to flush the trapped oil back to the sump63. This abrupt speed increase causes massive, temporary deviations in superheat, discharge temperature, and power consumption. A naive RUL model would interpret this extreme transient excursion as a sudden, severe fault.

### 4.2 The Necessity of Advanced Steady-State Filtering

To protect the prognostic algorithm from transient artifacts, including oil return flushes, defrost cycles, and standard startup sequences, the pipeline must incorporate a robust Steady-State Filter prior to residual calculation65. Relying on methodologies proposed by Li & Braun and Kim et al., data must only be passed to the residual generator if the system has achieved thermal equilibrium2.

A mathematically rigorous approach involves tracking the moving variance and the exponentially weighted moving average (EWMA) of critical driving variables (e.g., compressor speed, outdoor air temperature, and supply air setpoint).

The system is flagged as "steady" only when the short-term variance  falls below a dynamically calculated threshold  for a sustained temporal window (e.g., 10 to 15 minutes)65. All transient data is masked out. The RUL forecasting model (e.g., PatchTST) is then trained and executed exclusively on the concatenated sequence of steady-state residuals, which accurately represent the true underlying thermodynamic health of the equipment devoid of operational noise.

## 5. Architectural Methodology: From Classification to Forecasting

To successfully transition a point-in-time FDD classification pipeline to a continuous, predictive time-series forecasting system, the following modular, step-by-step methodology is recommended:

### Step 1: Telemetry Ingestion and Edge Filtering

- Action: Ingest high-frequency (e.g., 1-minute interval) IoT telemetry from the equipment, specifically targeting , , , , , , and compressor RPM.

- Gating Mechanism: Apply a moving-variance steady-state filter. Isolate and discard transient sequences caused by load changes, VFD oil return flush cycles, and defrost cycles64.

### Step 2: Healthy Baseline Modeling and Residual Generation

- Action: Input the steady-state boundary conditions (Source Temperature, Sink Temperature, Compressor Speed) into the existing healthy baseline model. This model is typically derived from fundamental thermodynamic properties (via tools like CoolProp) or empirical polynomial regressions established during the equipment's commissioning phase.

- Output: Calculate the predicted healthy state for critical internal variables (e.g., Expected Superheat, Expected Condenser Approach Temperature).

- Residual Calculation: Subtract the healthy prediction from the actual steady-state observation to generate a multivariate vector of residuals (e.g., , ). This effectively decouples equipment health from ambient weather and building load conditions.

### Step 3: Temporal Forecasting Engine (PatchTST)

- Action: Feed the historical time-series of the generated steady-state residuals into a PatchTST model, implemented via the Python neuralforecast library49.

- Configuration: Utilize the model's channel independence to process each residual type separately. Define a substantial look-back window (e.g.,  steady-state steps) and an appropriate patch length (e.g., ) to capture macro-degradation trends without overwhelming the attention mechanism49.

- Output: The model outputs a forecast of the residual trajectories over a defined future horizon (e.g.,  steps).

### Step 4: Prognostic Thresholding and RUL Estimation

- Action: Project the forecasted residual trajectories against pre-defined engineering failure thresholds. For example, ASHRAE Guideline 36 logic or manufacturer specifications may dictate that a condenser approach temperature residual exceeding +4.0°C indicates severe, efficiency-crippling fouling that risks compressor burnout70.

- Output: Calculate the Remaining Useful Life (RUL) as the exact time differential between the current operational timestamp and the future point at which the forecasted residual intersects the critical failure threshold72.

### Step 5: Edge Deployment and Optimization

For industrial IoT applications, transmitting high-frequency raw telemetry to the cloud for real-time inference is often cost-prohibitive, introduces latency, and raises data security concerns. Because PatchTST relies on highly efficient patch embeddings rather than dense token-by-token processing, its computational and memory footprint is remarkably small compared to traditional Transformers50.

The trained PatchTST model can be quantized (e.g., utilizing INT8 precision) and deployed directly on edge hardware. Recent benchmarks demonstrate that optimized time-series Transformers can execute with sub-millisecond inference latency on hardware as ubiquitous and inexpensive as a Raspberry Pi 4 or Nvidia Jetson Orin Nano75. This edge-native approach maintains strict energy budgets while providing localized, real-time RUL predictions directly at the HVAC/R asset, integrating seamlessly with local Building Management Systems (BMS).

#### Sources des citations

- Copyright Undertaking - PolyU Electronic Theses, https://theses.lib.polyu.edu.hk/bitstream/200/12488/3/6937.pdf

- Uncertainty analysis and field implementation of a fault detection, https://www.researchgate.net/publication/336347606_Uncertainty_analysis_and_field_implementation_of_a_fault_detection_method_for_residential_HVAC_systems

- Real-Time Prognostics of Engineered Systems under Time Varying, https://pmc.ncbi.nlm.nih.gov/articles/PMC7958339/

- An Analysis of Prognostics via Classification and Regression - arXiv, https://arxiv.org/pdf/2506.20090

- Direct remaining useful life prediction based on multi-sensor, https://www.jise.ir/x26url/x3dhttp:/www.jise.ir/article_105467_37e4da73a1e31d55eb7c2340433d683c.pdf

- Fault Characterization in ASHRAE RP-1043 - ResearchGate, https://www.researchgate.net/figure/Fault-Characterization-in-ASHRAE-RP-1043_tbl3_268127435

- An interpretable graph convolutional neural network based fault, https://www.sciopen.com/article/10.1007/s12273-024-1125-6

- Important sensors for chiller fault detection and diagnosis (FDD, https://www.researchgate.net/publication/245053092_Important_sensors_for_chiller_fault_detection_and_diagnosis_FDD_from_the_perspective_of_feature_selection_and_machine_learning

- LBNL FDD Data Sets - - Figshare, https://figshare.com/collections/LBNL_FDD_Data_Sets/6486349

- A labeled dataset for building HVAC systems operating in faulted, https://escholarship.org/content/qt07q164zx/qt07q164zx.pdf?v=lg

- LBNL FDD Data Sets Boiler Plant - figshare, https://figshare.com/articles/dataset/LBNL_FDD_Data_Sets_Boiler_Plant/22338238

- LBNL FDD Data Sets FCU - figshare, https://figshare.com/articles/dataset/LBNL_FDD_Data_Sets_FCU/22338256

- Datasets of Faults in Variable Air Volume Terminal Units in a Multi, https://pmc.ncbi.nlm.nih.gov/articles/PMC12062250/

- A labeled dataset for building HVAC systems operating in faulted, https://pmc.ncbi.nlm.nih.gov/articles/PMC10235024/

- Data Sets for Evaluation of Building Fault Detection and Diagnostics, https://data.openei.org/submissions/910

- Data Sets for Evaluation of Building Fault Detection and Diagnostics, https://www.osti.gov/biblio/1824861

- Data Sets for Evaluation of Building Fault Detection and Diagnostics, https://catalog.data.gov/dataset/data-sets-for-evaluation-of-building-fault-detection-and-diagnostics-algorithms

- Sensitivity Analysis of Installation Faults on Heat Pump Performance, https://nvlpubs.nist.gov/nistpubs/technicalnotes/nist.tn.1848.pdf

- Heating Mode Performance Measurements For A Residential Heat, https://nvlpubs.nist.gov/nistpubs/TechnicalNotes/NIST.TN.1648_2009.pdf

- FDD CX: A Fault Detection and Diagnostic Commissioning Tool for, https://tsapps.nist.gov/publication/get_pdf.cfm?pub_id=912311

- Method for Calculating Target Temperature Split, Target Superheat, https://patents.google.com/patent/US20110082651A1/en

- Residential heat pump heating performance with single faults imposed, https://www.researchgate.net/publication/232410900_Residential_heat_pump_heating_performance_with_single_faults_imposed

- Effect of Common Faults on the Performance of Different Types of, https://pmc.ncbi.nlm.nih.gov/articles/PMC4768314/

- HEAPO – An Open Dataset for Heat Pump Optimization with Smart, https://www.researchgate.net/publication/392745040_HEAPO_-_An_Open_Dataset_for_Heat_Pump_Optimization_with_Smart_Electricity_Meter_Data_and_On-Site_Inspection_Protocols

- The Development of a System to Analyze, Inspect and Predict in, https://www.ijert.org/the-development-of-a-system-to-analyze-inspect-and-predict-in-advance-the-failure-of-centralized-variable-refrigerant-flow-air-conditioners-using-machine-learning

- Equation-Based Object-Oriented Modeling and Simulation for Data, https://www.osti.gov/servlets/purl/1526586

- (PDF) Equation-Based Object-Oriented Modeling and Simulation for, https://www.researchgate.net/publication/330548514_Equation-Based_Object-Oriented_Modeling_and_Simulation_for_Data_Center_Cooling_A_Case_Study

- ElectricEIR with air-cooled condenser · Issue #2770 - GitHub, https://github.com/lbl-srg/modelica-buildings/issues/2770

- Diagram of Modelica model for a chiller with two variable speed, https://www.researchgate.net/figure/Diagram-of-Modelica-model-for-a-chiller-with-two-variable-speed-compressors_fig5_330548514

- Synergy between control theory and machine learning for building, https://www.researchgate.net/publication/358502904_Synergy_between_control_theory_and_machine_learning_for_building_energy_management

- (PDF) Reinforcement learning for HVAC control and energy, https://www.researchgate.net/publication/391018578_Reinforcement_learning_for_HVAC_control_and_energy_efficiency_in_residential_buildings_with_BOPTEST_simulations_and_real-case_validation

- Remaining Life Prediction of Shielding Sleeves Based on Data, https://www.mdpi.com/1424-8220/26/11/3367

- Health Assessment and Prognostics Based on Higher Order Hidden, https://arxiv.org/html/2002.05272v1

- Remaining Ueful Life Estimation—A Review on the Statistical Data, https://www.researchgate.net/publication/220289495_Remaining_Ueful_Life_Estimation-A_Review_on_the_Statistical_Data_Driven_Approaches

- TECHNICAL DIGEST - Arkema, https://www.arkema.com/files/live/sites/fluorogases_forane_arkema/files/downloads/literature/Forane%20Refrigerants%20Technical%20Digest%20EN

- Refrigerant blends may or may not have glide, which is a difference, https://www.facebook.com/hvacrschool/posts/refrigerant-blends-may-or-may-not-have-glide-which-is-a-difference-between-the-b/1466312955536716/

- EPA 608 Refrigerant Types Explained - VoltExam, https://www.voltexam.com/blog/epa-608-refrigerant-types-r22-r410a-r32-exam-guide

- A RUL Estimation System from Clustered Run-to-Failure ... - PMC, https://pmc.ncbi.nlm.nih.gov/articles/PMC9318987/

- The magic of the Kalman filter, in pictures : r/programming - Reddit, https://www.reddit.com/r/programming/comments/3gltt6/the_magic_of_the_kalman_filter_in_pictures/

- Extended Kalman Filter with Reduced Computational Demands for, https://www.mdpi.com/1424-8220/20/6/1584

- A Comparison of Nonlinear Filters on Mobile Robot Pose Estimation, https://scispace.com/pdf/a-comparison-of-nonlinear-filters-on-mobile-robot-pose-18vltvucwt.pdf

- A robust health prediction using Bayesian approach guided by, https://web.mae.ufl.edu/nkim/Papers/paper145.pdf

- Time Particle Filtering - Academic Commons - Stony Brook University, https://commons.library.stonybrook.edu/cgi/viewcontent.cgi?article=2514&context=stony-brook-theses-and-dissertations-collection

- arXiv:1912.02708v1 [eess.SP] 3 Dec 2019, https://arxiv.org/pdf/1912.02708

- Lithium-ion battery RUL prediction based on optimized VMD-SSA, https://pmc.ncbi.nlm.nih.gov/articles/PMC12287278/

- Application of a Kalman Filter and Particle Filter Fusion Model, https://www.researchgate.net/publication/398474418_Precise_Positioning_Method_of_Unmanned_Aerial_Vehicle_in_Enclosed_Environments_by_Integrating_Multi-Sensor_Information_Application_of_a_Kalman_Filter_and_Particle_Filter_Fusion_Model_Based_on_Dynamic_

- Data-driven approach to fault detection for hospital HVAC system, https://www.emerald.com/sasbe/article/15/2/765/1258758/Data-driven-approach-to-fault-detection-for

- Time-Series Foundation Model Embeddings for Remaining Useful, https://arxiv.org/html/2606.11990v1

- PatchTST Time Series Forecasting in Python - Nixtla - Nixtlaverse, https://nixtlaverse.nixtla.io/neuralforecast/models.patchtst.html

- Scaled FP32 and Quantization-aware Training of PatchTST for, https://kdd-milets.github.io/milets2025/papers/MILETS_2025_paper_17.pdf

- A Time Series is Worth 64 Words: Long-term Forecasting with ... - arXiv, https://arxiv.org/abs/2211.14730

- FASTTF - OpenReview, https://openreview.net/pdf/92ba4a9dad4014a96402df089cf717c05d7bea49.pdf

- GIFT-EVAL:ABENCHMARK FOR GENERAL TIME SE- | OpenReview, https://openreview.net/pdf?id=9EBSEkFSje

- SOFTS: The Latest Innovation in Time Series Forecasting, https://www.datasciencewithmarco.com/blog/softs-the-latest-innovation-in-time-series-forecasting

- pyFAST: A Modular PyTorch Framework for Time Series Modeling, https://www.researchgate.net/publication/394979090_pyFAST_A_Modular_PyTorch_Framework_for_Time_Series_Modeling_with_Multi-source_and_Sparse_Data

- HVAC Fault Detection & Diagnostics (FDD) - iFactory AI, https://ifactoryapp.com/industries/hvac/hvac-fault-detection-diagnostics-fdd-automated

- Detection and Diagnosis of Dependent Faults That Trigger False, https://www.researchgate.net/publication/358837831_Detection_and_Diagnosis_of_Dependent_Faults_That_Trigger_False_Symptoms_of_Heating_and_Mechanical_Ventilation_Systems_Using_Combined_Machine_Learning_and_Rule-Based_Techniques

- VFD Limitations for Residential HVAC Compressor Speed Control, https://industrialmonitordirect.com/blogs/knowledgebase/vfd-limitations-for-residential-hvac-compressor-speed-control

- Variable Frequency Drive Applications in HVAC Systems - IntechOpen, https://www.intechopen.com/chapters/49511

- VFD Control of Refrigeration Compressors - Industrial Monitor Direct, https://industrialmonitordirect.com/blogs/knowledgebase/applying-vfds-to-reciprocating-refrigeration-compressors

- How to Solve the High Pressure Fault and Oil Return Failure of, https://www.corestartech.com/blog/how-to-solve-the-high-pressure-fault-and-oil-return-failure-of-chiller/

- Danfoss training-common faults and analysis of compressors, https://okmarts.com/news/danfoss-training-common-faults-and-analysis-of-compressors.html

- Variable Speed Scroll Compressors: Why They Dominate Modern, https://hvacknowitall.com/blog/variable-speed-scroll-compressors-why-they-dominate-modern-heat-pumps

- Variable speed drive compressor control - TempMaster - OmniPremier, https://docs.johnsoncontrols.com/ductedsystems/r/TempMaster/en-US/OmniPremier-25-Ton-to-80-Ton-Rooftop-Units-R-410A-Start-Up-and-Operation-Guide/2022-02-02/Sequences-of-operation/Cooling-operation/Compressor-staging-sequences/Variable-speed-drive-compressor-control

- (PDF) An Adaptive Kalman Filter-Based Condition-Monitoring, https://www.researchgate.net/publication/370625246_An_Adaptive_Kalman_Filter-Based_Condition-Monitoring_Technique_for_Induction_Motors

- Development, implementation, and evaluation of a fault detection, https://www.researchgate.net/publication/343462690_Development_implementation_and_evaluation_of_a_fault_detection_and_diagnostics_system_based_on_integrated_virtual_sensors_and_fault_impact_models

- Modelling of small capacity absorption chillers driven by solar, https://www.tdx.cat/bitstream/10803/51878/1/PhD%20thesis%20Jlabus.pdf

- (PDF) Investigation of an IoT-Based Approach for Automated Fault, https://www.researchgate.net/publication/371982260_Investigation_of_an_IoT-Based_Approach_for_Automated_Fault_Detection_in_Residential_HVAC_Systems

- (PDF) An Autonomous Large Language Model‐Agent Framework, https://www.researchgate.net/publication/403243199_An_Autonomous_Large_Language_Model-Agent_Framework_for_Transparent_and_Local_Time_Series_Forecasting

- Performance Sequences of Operation for Multiple-Zone Variable Air, https://nvlpubs.nist.gov/nistpubs/TechnicalNotes/NIST.TN.2024.pdf

- ASHRAE Guideline 36 for Engineers: Practical Guide, https://futuregenconsulting.ca/ashrae-guideline-36/

- Tracking Predictive Maintenance KPIs for Rotary Screw Air, https://www.airbestpractices.com/sites/default/files/Tracking%20Predictive%20Maintenance%20KPIs%20for%20Rotary%20Screw%20Air%20Compressors.pdf

- A Review of Remaining Useful Life Prediction Approaches for, https://www.researchgate.net/publication/375478152_A_Review_of_Remaining_Useful_Life_Prediction_Approaches_for_Mechanical_Equipment

- Deploying time-series transformers on embedded FPGAs, https://nbn-resolving.org/urn:nbn:de:hbz:465-20260415-092644-6

- Deep Climate Model Distillation for Localized Flood Forecasting in, https://www.mdpi.com/2674-0494/5/2/16

- Industrial AI & Analytics: Predictive, Vision, OEE - Suriota, https://suriota.com/ai-industrial-analytics/

- Spatio-Temporal Neural Rendering: Reversible Time-to-Vision, https://www.computer.org/csdl/journal/tm/2026/06/11341902/2ddLqIEEe08